School Pre-Opening Checklist

General

☐	Building is designed to provide >21 cfm of airflow per person in each room

☐ 	HVAC system is functional and on at time of inspection

☐ 	Custodial closets have negative air pressure

☐ 	Provide local exhaust ventilation for 3-D printers, printers, copiers and laminators and other equipment that produces volatile organic compounds (VOCs)

☐ 	Provide 30 foot candles of light at all desks/work surfaces in classrooms/libraries/study rooms

☐ 	Provide 10 foot candles of light in all hallways

☐ 	Background noise levels measure 45 dBA or lower in all classrooms.

☐ 	Secure all bookcases and shelving over 4 feet high

☐ 	Ensure outlets within 6 feet of a water source are protected by ground fault circuit interruption (GFCI)

☐ 	Ensure upper story windows do not open >4 inches and window coverings present

☐ 	Door sweeps are installed on all exterior doors

☐ 	Provide walk off mats at all entryways

☐ 	Ensure temperature is at least 65° F in all rooms and hallways

Health room

☐	Ensure health room has negative air pressure to surrounding rooms

☐	Provide locking storage for medications (including options for refrigerated items)

☐ 	Provide 10 foot candles of light in the health room

Bathrooms

☐ 	Bathrooms have negative air pressure to surrounding rooms

☐ 	Provide 10 foot candles of light in all bathrooms

☐ 	Stock all handwash sinks with soap and paper towels

☐ 	Ensure handwash sinks provide hot water between 90°-120° F

☐ 	Ensure self-closing faucets provide at least ten seconds of continuous water flow

☐ 	Provide sanitary napkin bins in girls’ bathrooms

Gym

☐ 	Provide 20 foot candles of light in all gyms/locker rooms

☐ 	Provide wall pads behind basketball hoops

☐ 	Ensure showers provide hot water between 100°-120° F

☐ 	Ensure room temperature is at least 60° F

Specialty Classrooms (Shop/CTE/Science Labs/Art)

☐ 	Ensure rooms have negative air pressure

☐ 	Make sure on-demand ventilation (for science labs) is functional

☐ 	Provide exhaust ventilation for all kilns

☐ 	Make sure sawdust collection system is installed/connected to equipment and

operates at 65 dBA or lower

☐ 	Provide 50 foot candles of light at all desks/work surfaces in special instruction areas,

including chemical storage rooms

☐ 	Make sure emergency eyewash station:

- Is installed as required

- Provides water flow of 0.4 gallons per minute for 15 minutes

- Has tepid water temperature of 60-100°F

- Has eyewash caps that are easily dislodged when activated

- Requires only 1-step activation

- Is plumbed to a floor drain to allow for easy testing

☐ 	Make sure emergency shower:

- Is installed as required

- Provides water flow of 20 gallons per minute for 15 minutes

- Has tepid water temperature of 60-100°F

- Requires only 1-step activation

- Is plumbed to a floor drain to allow for easy testing

☐ 	Ensure fume hood is installed as required and has documentation of testing

☐ 	Ensure fume hood is calibrated to provide at least 60 linear feet per minute of

ventilation with the sash positioned at 12 inches

☐ 	Make sure flammables cabinet is installed as required and has doors that self-close

☐ 	Ensure chemical storeroom has:

- Earthquake spill-prevention lips installed on shelving for chemicals/glassware

- A door that self-closes and locks

- A door with a fire rating of at least 1 hour

☐ 	Make sure emergency shut-off switches (electrical/gas) are installed, labeled,

functional, and accessible

☐ 	Provide first aid kit

☐ 	Provide spill clean-up kit

☐ 	Install non-slip flooring within the operator use zones of shop equipment

☐ 	Provide safety/use zones around all shop equipment, recommend at least 2-foot zone

☐ 	Post shop safety rules

☐ 	Post shop equipment operating instructions/safety reminder signs

☐ 	Provide fire extinguishers/fire blankets